The Proposed Development will consist of a 10 year permission for a 110kV electrical substation and associated 110kV underground grid connection, cabling and associated works. The Proposed Development will transmit power from a solar farm (permitted under Tipperary County Council Reg. Ref: 21/1128), which will connect into the existing Lisheen 110kV ESB substation.

The proposed 110kV electrical substation in Killoran, on a site of 2ha will consist of:

- 1 no. electrical substation compound and access road, palisade fencing and gates;

- 1 no. electrical substation compound / IPP control building measuring 10.74m x 20.15m and 6.920m in height;

- Station compound extension required at Lisheen 110kV station to facilitate the new Cooleeny 110kV cable bay;

- 1 no. Eirgrid switch room building measuring 18m x 25m and 8.55m in height;

- 1 no. lightning protection monopoles measuring up to 22m in height;

- A main step-up transformer;

- Associated ancillary equipment such as electrical apparatus, plant and equipment;

- Overhead and underground electrical and communications cabling and ancillary works; and,

- All associated ancillary works above and below ground including raising a portion of the site by ca.1m using imported engineering fill;

The 110kV underground cabling is proposed from the proposed 110kV substation to the existing Lisheen 110kV ESB substation, will consist of:

- Ca. 225m of underground 110kV electrical cables and associated communications cables;

- Three 125mm diameter HDPE power cable ducts;

- One 100mm diameter HDPE communications ducts;

- One 125mm diameter earth continuity duct to be installed in an excavated trench, typically 825mm wide by 1,315mm deep;

- 1600sq mm Al cable;

- 240sq mm copper earth continuity cable;

- One fibre cable; and,

- All associated ancillary works above and below ground.